{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":44,"n_cols":9,"rows_kept":44,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","2MXM-M"]
[]
[]
[]
[]
["","","","","","2MXM40M2V1B","2MXM40M4V1B","2MXM40M3V1B","2MXM50M2V1B"]
["Вентилятор","Расход воздуха","Охлаждение","Сверхнизкий","м³/мин","30","","","34"]
["","","Нагрев","Сверхнизкий","м³/мин","32","","","34"]
["","","","Вентилятор-=-Расход воздуха-=-Охлаждение-=-Сверхнизкий-=-фт3/мин","куб. фт/мин","1059","","","1200"]
["","","Нагрев","Вентилятор-=-Расход воздуха-=-Нагрев-=-Сверхнизкий-=-фт3/мин","куб. фт/мин","1130","","","1200"]
["Размеры","Блок","","Размеры-=-Блок-=-Высота-=-мм","мм","550","550","550","550"]
["","","","Ширина","мм","765","765","765","765"]
["","","","Глубина","мм","285","285","285","285"]
["Масса","Блок","","","кг","36","36","36","41"]
["Двигатель вентилятора","Скорость","Охлаждение","Самый низкий","об/мин","760","500","500","890"]
["","","Нагревание","Самый низкий","об/мин","820","320","320","890"]
["Компрессор","Type","","","","Герметичный компрессор ротационного типа","Герметичный компрессор ротационного типа","Герметичный компрессор ротационного типа","Герметичный компрессор ротационного типа"]
["Рабочий диапазон","Охлаждение","Темп. нар. возд.","Мин.","°CDB","-10","-10","-10 (2)","-10"]
["","","","Макс.","°CDB","46","46","46 (2)","46"]
["","Hагрев","Темп. нар. возд.","Мин.","°CWB","-15","-15","-15","-15"]
["","","","Макс.","°CWB","18","18","18","18"]
["Уровень звукового давления","Охлаждение","","Уровень звукового давления-=-Охлаждение-=-Выс.-=-дБ(A)","дБ(A)","","46","46"]
["","","","Уровень звукового давления-=-Охлаждение-=-Ном.-=-дБ(A)","дБ(A)","48","","","46"]
["","Hагрев","","Уровень звукового давления-=-Hагрев-=-Выс.-=-дБ(A)","дБ(A)","","48","48"]
["","","","Уровень звукового давления-=-Hагрев-=-Ном.-=-дБ(A)","дБ(A)","50","","","48"]
["Хладагент","Тип","","","","R-32","R-32","R-32","R-32"]
["","Заправка","","","кг","0.88","0.88","0.88","1.15"]
["","Заправка","","","tCO2Eq","0.6","0.60","0.59","0.8"]
["","ПГП","","","","675","675","675","675"]
["Подсоединение труб","Длина трубы","Макс.","НБ - ВБ","м","20","20","20 (1)","20"]
["Подсоединения труб","Дополнительная заправка хладагента","","","кг/м","0,02 (для длины труб свыше 20 м)","0,02 (для длины труб свыше 20 м)","0,02 (для длины труб свыше 20 м)","0,02 (для длины труб свыше 20 м)"]
["","перепад уровня","IU - OU","Макс.","м","15","15.0","15.0","15"]
["","","IU - IU","Макс.","м","7.5","7.5","7.5","7.5"]
["Подсоединение труб","Общая длина трубопроводов","Система","Фактическая","м","30","30","30","30"]
["Стандартные аксессуары","Installation manual","","","","Installation manual","1","1","1"]
["","Drain plug","","","","Drain plug","1","1","1"]
["","Screw bag","","","","Screw bag","1","1","1"]
["Электропитание","Фаза","","","","1~","1~","1~","1~"]
["","Частота","","","Гц","50","50","50","50"]
["","Напряжение","","","V","220-240","220-230-240","220-230-240","220-240"]
["Примечания","","","","","","(1) - Для одного помещения"]
["","","","","","","","(1) - Для одного помещения"]
["","","","","","","","(2) - Рабочий диапазон см. в отдельных чертежах"]
["Стандартные аксессуары","Reducer assembly","","","","","","","1"]